## Slide 1: Control Technology Incorporated

## Slide 2: Product Spotlight Redundancy & Backup Solutions – Remote Bases
Redundant RBC
Redundant power
Redundant power & redundant RBCs

## Slide 3: Product Spotlight Redundancy & Backup Solutions – Processors
Redundant power with one CPU

## Slide 4: Product Spotlight Redundancy & Backup Solutions – Processors
Redundant power & redundant CPUs using Redundant Processor Manager
To remote bases

## Slide 5: Backup CPU with Redundant RBCs Using independent cables to RBCs
termination
primary
backup

## Slide 6: Using the 2541 Redundant Processor Manager

## Slide 7: 2541 Redundant Processor Manager
“Warm” Backup for Simatic TI505 PLCs
  Asynchronous program execution between two CPUs
  Both CPUs see all the I/O
  Transfer within 100ms or 2 scans
“Bumpless” transfer
  Transfer of control without changing the outputs

## Slide 8: How Does the RPM Work?
Communicates with both PLCs using the remote I/O connection
I/O is attached to the PLC in control using relay contacts
Both PLCs see the field inputs all the time
Monitors both PLCs and switches the I/O to the backup PLC in case of fault
Creates “virtual bases” that appear in both PLCs
  Both PLCs and RPM can monitor all status information
  Critical data is written to the backup PLC

## Slide 9: Configuration Example 1
RPM Installed in rack with PLC B
Uses backplane for power only
Both PLCs are connected to the RPM module
Remote I/O is connected to the RPM module
PLC A
PLC B
I/O

## Slide 10: Configuration Example 2
RPM installed in separate rack
Uses backplane for power only
Both PLCs are connected to the RPM module
Remote I/O is connected to the RPM module
PLC A
PLC B
I/O
RPM

## Slide 11: MMI Connection Example
PLC A
PLC B
I/O
MMI

## Slide 12: RPM Front Panel
Module Status and Configuration Section
Serial Port, Status LEDs, Resume Button
PLC A Section
Connectors, Status LED, Transfer Button
Remote I/O and HMI Connectors
PLC B Section
Connectors, Status LED, Transfer Button

## Slide 13: RPM Front Panel (top)
MODULE IN CONTROL LED
When ON, this module is controlling the switching
MODULE GOOD LED
When ON, the module is functioning properly
CONFIGURATION PORT
Configuration Port with signal LEDs
RESUME SWITCH
Press to resume operation after a module fault

## Slide 14: RPM Front Panel (mid)
PLC A ACTIVE LED
ON solid when PLC A is PLC in control
Blinking when PLC A is available for transfer
TRANSFER TO PLC A Switch
Request switchover to PLC A
PLC B ACTIVE LED
ON solid when PLC B is PLC in control
Blinking when PLC B is available for transfer
TRANSFER TO PLC B Switch
Request switchover to PLC B

## Slide 15: RPM Front Panel (lower)
Reserved for Backup RPM
Not yet implemented
Remote I/O and HMI Connectors

## Slide 16: RPM Internal Diagram
Directly connects I/O to the active PLC through a relay contact
Monitors active and standby PLC
Sends input values to standby PLC
Sends virtual base data to standby PLC
Switches to standby PLC when a specified event occurs
PLC A
PLC B
Mirror Memory for I/O and (virtual bases)
RPM MODULE
Remote I/O

## Slide 17: Transfer Conditions
Automatic transfer
  Active PLC I/O update not received within a specified time
  Active PLC “Heartbeat” not received within a specified time
  RPM detects a fatal error in Active PLC
Manual transfer
  PLC logic requests a transfer of control
  Module pushbutton requests a transfer of control
Will not transfer if
  Standby PLC is not operational (ie fatal error or no I/O scan)
  Standby PLC program does not match Active (optional)
  Disabled by user in configuration program

## Slide 18: Module Fail-Safe Operation
Fail Safe mode activated when there is an RPM problem
Conditions to activate fail-safe
  Loss of power to RPM
  Early Power Fail is detected
  RPM diagnostics detect an error
  Watchdog timer trip
Action for fail-safe
  Module defaults to a predetermined relay state
    Hardware Controlled
    Set by a switch on the board
  Remote racks are connected to the predetermined PLC
  If triggered by watchdog timer, the module remains in this state until user intervenes

## Slide 19: Other RPM Functions
MMI Switching
  Includes serial operator panels, TCAMs, etc.
  Transfer follows the remote I/O switchover
PLC Data Transfer
  Copies data from the Active PLC to the Standby PLC
    Values that are required to prevent program divergence
    Values that can’t be obtained via I/O image register
    May include timers counters, drums, loops, etc.
  Critical Data - Transfer Every Scan
  Normal Data - Transfer over several Scans

## Slide 20: Critical Data Transfer & Control
RPM creates “Virtual Bases” which appear to both PLCs
  Up to 16 32WX/32WY modules
Data Transfer
  Active PLC logic writes to virtual base WY’s
  RPM copies WY value to a corresponding WX value
  Standby PLC logic reads from virtual base WX’s
Logic must be conditioned on “Active” bit from RPM
  Shows as a 1 for active PLC
  Shows as a 0 for standby PLC

## Slide 21: Creating Virtual Bases for Critical Data Transfer
Created using the 2541 configuration program
A virtual base appears in both PLCs
  Looks just like a real base
  Can be assigned any address not in use by a real base
You must create at least one virtual base (home base)
  Used to transfer status bits for the RPM system to both PLCs
  Contains up to 16 virtual modules
  2 virtual discrete modules, one 32X, one 32Y
  Can contain up to 14 virtual word modules (32WX, 32WY)
Additional virtual bases contain only virtual word modules
Logic is required in both PLCs and they must know whether they are in ‘active’ or ‘standby’

## Slide 22: Non-critical Data Transfer
Configured in RPM module, no PLC logic required
Data Transfer
  RPM reads from specified V memory block in active PLC
  RPM writes to corresponding V memory block in standby PLC
Transfer takes multiple scans

## Slide 23: RPM Status Bits (X values in home base)
Offset | Description
0 | PLC A has active control (1 = Yes, 0 = No)
1 | PLC B has active control (1 = Yes, 0 = No)
2 | PLC Active Flag (1 = this PLC is active, 0 = this PLC is standby)
3 | PLC A Status (1 = Operational, 0 = Not Operational)
4 | PLC B Status (1 = Operational, 0 = Not Operational)
5 | Checksum Compare (1 = Checksums match, 0 = Checksums do not match)
6-8 | Reserved
9 | Non-Critical Data Transfer Completed - Alternates with offset 10
10 | Non-Critical Data Transfer Completed - Alternates with offset 9
11 | RPM has control (reflects I/O update monitoring status, 1=enabled,0=disabled)
12 | Reserved for future use
13 | RPM module is good (operational)
14-15 | Reserved
16 | I/O Update Monitor Enable (1=Enabled, 0=disabled)
17 | Heartbeat Monitor (1=Enabled, 0=disabled)
18 | PLC Fatal Error Monitor (1=Enabled, 0=disabled)
19 | PLC Logic Transfer (1=Enabled, 0=disabled)
20 | Program Checksum Match (1=Enabled, 0=disabled)
21 | Front Panel Pushbutton Transfer (1=Enabled, 0=disabled)
22 | Switchover Enabled
23-31 | Reserved

## Slide 24: RPM Control Bits (Y values in home base)
Offset | Description
0 | Request Switchover to PLC A
1 | Request switchover to PLC B
2 | Heartbeat bit. PLC Logic must transition this bit every scan
3 | Switchover Inhibit
4-31 | Reserved for future use

## Slide 25: Setting up an RPM Application
Select wiring configuration and fail-safe operation
Identify critical and non-critical variables
Wire the system
Configure fail-safe and RTS on RPM
Configure the module using software
  Setup switchover operation
  Setup virtual bases and real bases
Add PLC logic to copy critical and non-critical data
Test

## Slide 26: Setup of Fail-safe and RTS
Set fail-safe switch for PLC A or PLC B
Set RTS-COM switch to COM unless using RF converter

## Slide 27: Software Configuration of the RPM
Install Windows configuration program
Attach to module using serial cable (TISOFT cable)
Run program and open port to 9600,odd, 7,1
Configure transfer options and bases
RPM Configuration

## Slide 28: RPM Summary
Provides Warm Backup for TI505 PLCs
  Automatically switches remote I/O and HMI
  Provides data transfer between PLCs
Directly connects active PLC with remote I/O
  No intervening electronics
  Fail-safe default selection (hardware)
Software configurable options
  Specify switchover options
  Establish virtual bases and non critical data transfer